## Slide 1
www.ifrc.org
Saving lives, changing minds.
Suprio Das

## Slide 2: Introduction
Zimba is a device which disinfects drinking water by automatically dosing it with chlorine
Zimba automatically mixes chlorine into drinking water in the correct proportions, regardless of the flow rate of the water
The device can be fitted to a community’s existing water source with intermittent flow such as:
  the hand pump of a well;
  the tap of a rainwater harvesting cistern;
  or the tap of a piped water system;

## Slide 3: Advantages of using Zimba
The main advantages of Zimba in respect to other similar devices are:
It is simple to use, it was designed without moving parts such as hinges and gears that are known to be the first point of failure in most technical complex designs.
It is easy to install and maintain, it does not require electricity, uses only gravity to operate and can handle thousands of litres per day.
Users do not have to change behaviour in the way they collect water.
Any chlorine solution dilution can be used, and the device is adjusted (The device may be adjusted to suit very low concentration of chlorine solution too).

## Slide 4: Video on how to assemble Zimba

## Slide 5: Disassembly
Notes: Step 1: Gently unpack the device
Step 2: Remove the packing tape and unlock

## Slide 6: Disassembly
Notes: Step 3: Remove chlorine chamber and siphon carefully (Do not lift the siphon by bell, lift only by sidewall)

## Slide 7: Additional parts
The tap and plug should be fitted using plumbers’ tape to achieve a good seal.
Alternatively a flexible hose can replace the faucet.
These are provided with each Zimba unit
Notes: Step 4: Use plumber tape to seal and attach tap and stopper to Zimba housing (two people required)

## Slide 8: Priming the siphon
Notes: Step 5: Prime siphon by filling with water

## Slide 9: Zimba functioning

## Slide 10: Reassembly
Notes: Step 6: Reinsert siphon and chlorine chamber
Step 7: Add chlorine, do not overfill (Use gloves and eye protection when using real chlorine)

## Slide 11: Filling chlorine chamber

## Slide 12: Adjusting the dose to minimum
Notes: Step 8: Start with lowest setting and adjust dose upward for optimal level to achieve residual chlorine.
Zimba adds a pre-set volume of chlorine per batch of water that is pumped in, through an automatic siphon.
It dispenses a dose between 2.5 to 6.0 mL of NaOCl solution into the siphon tank every L-batch of (approximately 12 L) water that flows through the device.

## Slide 13: Securing the chlorine chamber

## Slide 14: Lock then ready for use
Notes: Step 9: Replace lid, add gauze and lock firmly to reduce risk to children. (Remember chlorine burns)
Step 10: Zimba is now ready to use. Test treated water for residual chlorine after 30 minutes.

## Slide 15: Lock then ready for use
Weight of the each Zimba unit without chlorine solution is 10 kg.
Capacity of chlorine tank is 3 litre.
Flush volume is approximately 12 litre.
Average flushing speed is 55 litre per minute.
Dose volume is variable between 2.5 ml and 6.0 ml.
Except for the food grade fiberglass outer casing, all other components are made of recyclable Polypropylene.
All metallic nuts and bolts are of Stainless Steel.

## Slide 16: Precautions
Make sure the blue cap screws on well after dose adjustment to make an air-tight seal
The Zimba unit (or the stand) should be places in a flat level place. Tilting may result in malfunction of the device
Avoid spilling chlorine solution while refilling
If required, use the vent at the rear right corner of the dispenser to drain out chlorine solution from the dispenser
THE FLOW OF UNTREATED WATER SHOULD NOT EXCEED 15 LITRES PER MINUTE (a cup with a hole is included in the inlet to ensure the flow does not exceed this rate)

## Slide 17: Chlorine dose adjustment
The dose volume required will depend on:
Concentration of chlorine solution in the reservoir of the dispenser
Chlorine demand of untreated water
Required level of residual chlorine in output water. During cholera outbreaks WHO recommends a minimum free chlorine residual of 2.0 mg/L at the point-of-filling for tanker trucks, 1.0 mg/L for standpipes and wells, and 0.2−0.5 mg/L at point-of-use. (not more than 2mg/L or it affects taste)*
To begin, we recommend using 0.5% chlorine solution in the reservoir and the lowest setting of the dose. If output is lower than required, increase the dose to get the desired output concentration.
After adjustment, discard 5 flushes before measuring chlorine in output water.
*World Health Organization. Chlorine monitoring at point sources and in piped distribution systems. Fact Sheet 2.30. Geneva, Switzerland: World Health Organization; 2016. http://www.who.int/water_sanitation_health/hygiene/emergencies/fs2_30.pdfpdf iconexternal icon
Notes: Zimba adds a pre-set volume of chlorine per batch of water that is pumped in, through an automatic siphon.
It dispenses a dose between 2.5 to 6.0 mL of NaOCl solution into the siphon tank every L-batch of (approximately 12 L) water that flows through the device.
SL use WATA device
Kenya use MSR chlorine 0.8%
Recommend to buy locally produced chlorine (liquid bleach that can be found in the market) 0.5% chlorine solution up to 0.7 or 0.8 is fine.

## Slide 18: Quick method to estimate the dose volume per batch
(a) Hold water from entire flush (without chlorine) in a plastic bucket.
(b) Measure out 3 ml of available chlorine solution with an injection syringe (needle safely discarded).
(c) Add this 3 ml of chlorine solution to the bucket of water and stir with a non-metallic rod/stick.
(d) Check the ‘Free Residual Chlorine’ (FRC) level of the chlorinated water in the bucket. (see next slide for details)
(e) If the FRC level is not adequate, either add more chlorine to the same water (in 0.5ml increments) or use a higher concentration of chlorine in another bucket of untreated water, till the required level of residual chlorine is reached.
(f) Take another reading after 30 mins if the required level of residual chlorine is achieved. Keep in mind that the dose volume can only be varied between 2.5 and 6.5 ml – once decided, set the dispenser to that level and repeat to ensure it’s working correctly.
(g) Avoid exposing the water or the chlorine solution to sunlight during this exercise.
Notes: Discuss Issues/ challenges with installation/ use – 30’
Dosage – different water quality. Those who install would also need to test the water.
Taste and smell of chlorinated water not always liked by communities. Managing strategies – start with very low dose and increase gradually, week by week (Suprio to demonstrate use of chlorine doser)
Available chlorine solution (before training, make sure that this is purchased) > 4%, to be diluted to 0.5% or 1%
Discuss chlorine making devices, to produce chloring (SL > needs stabiliser solution). Suggest that concentrated liquid chlorine (bleach) is purchased and stored, and MSR/ WATA are kept for emergency use. Investigate what types of bleach is available on the market and choose best fit.

## Slide 19: Chlorine storage
Sodium hypochlorite is highly reactive and volatile. Never store in metal containers as chlorine will react with the metal.
Store or transport always in opaque plastic containers to prevent exposure of the solution to UV radiation from sunlight, which will decrease its shelf life.
In case the available chlorine solution is of a higher concentration than what is needed in the Zimba unit, you may have to dilute with water (e.g. 4%, dilute to 0.5% for use).
Never store diluted chlorine – dilute the solution at site just before refilling. Dilution reduces the pH value, which makes the solution unstable and thereby reduces shelf life. Sodium Hypochlorite solutions are comparatively stable at pH values above 11 when stored in opaque plastic containers.
(Source Zimba water webpage)
Notes: Method to stabilize the chlorine solution: Stabilizer provided by WATA WataStab™
Description: The WataStab™ ensures a minimum of 3 months stabilization of your sodium hypochlorite solution.
This ready-to-use kit can stabilize up to 1 000 L of sodium hypochlorite without any additional consumable. You will then be able to find this consumable in any local shop. Link: https://watatechnology.com/en/products-and-services/
http://zimbawater.com/technology/chlorine/
Dilution ratio
Let's try with the dilution they have, if the dilution is too high suggest how to dilute. From 4 to 1 part: three part of water and one part of chlorine. If they have 0.8 check if work

## Slide 20: Troubleshooting
SIPHON NOT FLUSHING
Water inflow into Zimba is greater than 15 litres/min. Open cover and siphon out water from the siphon tank using a flexible pipe. OR Water in U-tube of siphon dried up due to non-use for long period. Prime siphon and restart.
NO DOSING / CHLORINE IN OUTPUT WATER
No chlorine solution in reservoir. OR Dose-adjuster cap not tightened enough to seal air leaks.
EXCESS CHLORINE IN OUTPUT WATER
Damage in dispenser resulting in chlorine leak. Bring out the dispenser and fill it up with water or chlorine solution. Keep it in an upright position over a dry surface and observe for at least 30 min for any dripping. Report the matter to Zimbawater.
WATER COMING OUT FROM OVERFLOW VENT
Overflow will occur it the inflow exceeds outflow. Overflowing water is also chlorinated and may be collected in a bucket for use.