IFRC WASH TOOL · TROUBLESHOOTING CHART

Troubleshooting chart: boreholes with submersible pumps

Module 2, Topic 9: Boreholes with submersible pumps  ·  Troubleshooting chart  ·  Curriculum pp. 60–61

Potential unexpected problems, their probable causes and possible solutions. Use this chart in training and keep a copy at the site. Seek technical assistance if a problem cannot be solved with these steps.

| Problem | Probable cause | Possible solution |
| --- | --- | --- |
| Pump fails to start | • Broken or loose electric connection • Blown fuse - check the installation before replacing fuses • Motor overload • Low voltage • Damaged supply cable insulation; check insulation resistance • Cable - cable joint or motor windings may be wet or earthed • Impeller plugged • (Pump blocked with sand) | • Check power source. • Check switches. • Check fuses. • Call for technical assistance. |
| No water from borehole | • No power to pump • Pump is faulty and not working • Pump not submerged (pump set too high or water level has fallen) • Pump rotating in the wrong direction • Leak(s) in riser pipe joints or corroded pipe • Riser pipe joint threads corroded and disconnected • Non-return valve in pump blocked or corroded • Valves or discharge line blocked, damaged or not fully open • Worn pump due to pumping sand or other particles • Blocked or damaged borehole screen • Pumping head too high for pump • Strainer or impellers blocked with sand or chemical deposits | • Check power source. • Check switches. • Check fuses. • Check depth of water in borehole. • Call for technical assistance. |
| Pump turns on and off frequently | • Excessive drawdown • Capacity of pump exceeds borehole yield so water level drops below level of pump | • Call for technical assistance to investigate in detail. This may require test pumping, monitoring water level in borehole, changing pump, or lowering pump in borehole. |
| Pump overload switch trips out | • Current overload or motor temperature sensor - possible causes: blockage, insufficient flow of water over motor, overload due to mechanical problems, low voltage • Under-voltage - low voltage on supply system • Incorrect oil level in dashpot operated overloads • Low-level cut-out – excessive drawdown • Incorrect overload settings | • Call for technical assistance. • Check all settings. |
| Borehole delivering less water than expected | • Screens are blocked • Leaks in riser pipe | • Call for technical assistance to determine whether plunging of the borehole will result in improved yield. • Remove riser pipe and repair or replace. |
| Persistent case of sediments in borehole water (i.e., not immediately after borehole development) | • Sediments are passing through the screens | • Depending on the nature of the sediments, the sediments may be damaging to the pump. • Check the water quality. |
| Water quality is too saline | • Water in the aquifer is saline | • This is a feature of the aquifer and only surface treatment of the water (through reverse osmosis) can be used to make water potable. |