IFRC WASH TOOL · TROUBLESHOOTING CHART

Troubleshooting chart: diesel-powered generators

Module 2, Topic 14: Diesel-powered generators  ·  Troubleshooting chart  ·  Curriculum pp. 98–100

Potential unexpected problems, their possible causes and the remedy. For each problem the possible causes (a, b, c…) and remedies (a, b, c…) are listed in the same order. Specific requirements for each make and model are in the manufacturer's Operators Manual.

| No. | Problem | Possible cause | Remedy |
| --- | --- | --- | --- |
| 1 | Will not start: (i) engine does not turn | Battery is flat or has failed | (a) Check the liquid level; fill if necessary. Recharge the battery and check that all cells are working. (b) Replace the battery if it has failed. |
|  |  | Starter circuit faulty | (a) Check, clean and refit the battery connections. (b) Check the circuit relay and starter solenoid. |
|  |  | Starter faulty | (a) Replace the motor. Check that the starter is engaging; attempt to turn the engine by hand. |
|  |  | Lubricating oil too thick | Replace with the correct grade of oil. |
|  |  | Engine or alternator jammed | Inspect and remove any obstruction. |
| 1 | Will not start: (ii) engine turns but does not fire | (a) No fuel atomizers (b) Air in fuel system (c) Dirty fuel or water in the fuel (d) Faulty lift pump (e) Faulty injection pump (f) Injection timing wrong | (a) Check there is fuel available in the tank. Check that all fuel valves are open. (b) Bleed the fuel system. (c) Clean or replace the fuel filter. (d) Check the fuel lift pump. (e) Check the fuel injection pump. (f) Reset the injection pump timing. |
| 1 | Will not start: (iii) engine fires but fails to start | (a) Limited fuel supply (b) Faulty lift pump (c) Faulty injection pump (d) Fuel filter blocked (e) Air filter blocked (f) Worn or dirty injectors | (a) Bleed the fuel system and check it thoroughly for evidence of dirt or water. (b) Service the fuel lift pump. (c) Service the injection pump. (d) Clean or replace the fuel filter. (e) Clean or replace the air filter. (f) Service or change injectors. |
| 2 | Starts but misfires | (a) Limited fuel supply (b) Faulty lift pump (c) Faulty injection pump (d) Fuel filter blocked (e) Worn or dirty injectors (f) Loose or broken pipes (g) Incorrect valve clearances | (a) Bleed the fuel system and check it thoroughly for evidence of dirt or water. (b) Service the fuel lift pump. (c) Service the injection pump. (d) Clean or replace the fuel filter. (e) Service or change the injectors. (f) Tighten or replace the pipes. (g) Reset the valve clearances. |
| 3 | Starts but loses power | (a) All possible causes shown under 2 above (b) Air filter blocked (c) Faulty cylinder head or inlet manifold joints (d) Damaged or dirty turbocharger | Attention as shown in (a) to (g) above (under item 2 above). (i) Clean or replace the air filter. (j) Replace the gasket. (k) Clean or replace the filter. |
| 4 | Excessive fuel consumption | (a) Faulty injection pump (b) Worn or dirty injectors (c) Incorrect valve clearance (d) Fuel pump timing incorrect (e) Incorrect fuel (f) Excessive engine wear | (a) Service the fuel injection pump. (b) Service or change the injectors. (c) Reset the valve clearance. (d) Reset the fuel pump timing. (e) Check the fuel specification. (f) Overhaul the engine. |
| 5 | Black exhaust smoke | (a) Faulty injection pump (b) Worn or dirty injectors (c) Air filter is blocked (d) Fuel pump timing incorrect (e) Incorrect fuel (f) Damaged or dirty turbocharger (g) Excessive load (h) Long running time on light load | (a) Service the fuel injection pump. (b) Service or change the injectors. (c) Clean or replace the air filter. (d) Reset the fuel pump timing. (e) Check the fuel specification. (f) Clean or replace the turbocharger. (g) Reduce the load as necessary. (h) Run on full load for a one-hour period. |
| 6 | Blue/white exhaust smoke | (a) Engine misfiring (b) Excessive engine wear | (a) See remedy under item 2 above. (b) Overhaul the engine. |
| 7 | Low lubricating oil pressure | (a) Low oil level in sump (b) Oil pressure gauge faulty (c) Oil filter blocked (d) Faulty relief valve (e) Oil pump worn (f) Excessive oil temp | (a) Add lubricating oil to normal level. (b) Replace the oil-pressure gauge. (c) Clean or replace the oil filter. (d) Clean or replace the relief valve. (e) Replace the oil pump. (f) See the problem outlined in item 8 below. |
| 8 | High engine temperature | (a) Low level of coolant (b) Faulty thermostat (c) Fan belt slipping (d) Radiator matrix blocked (e) Blockage in cooling system (f) Low level of lubricating oil (g) Fuel injection pump's timing is incorrect (h) Cylinder head gasket failed | (a) Refill the radiator and check for any leaks. (b) Check and replace the thermostat if necessary. (c) Adjust the tension of the fan belt. (d) Clean out the radiator thoroughly. (e) Drain the system, flush it out and refill. (f) Refill the lubricating oil to the correct level. (g) Reset the timing of the fuel injection pump. (h) Remove the cylinder head and replace the gasket. |