IFRC WASH TOOL · TROUBLESHOOTING CHART

Troubleshooting chart: intakes (spring, river and infiltration gallery)

Module 2, Topic 7: Intakes  ·  Troubleshooting chart  ·  Curriculum pp. 51–52

Potential unexpected problems, their probable causes and possible solutions. Use this chart in training and keep a copy at the site. Seek technical assistance if a problem cannot be solved with these steps.

For spring intakes

| Problem | Probable cause | Possible solution |
| --- | --- | --- |
| Leaking gate valve | • Worn-out valve | • Replace the ‘stuffing’ box packing in gate valve or replace entire valve. |
| Little or no water flowing into intake chamber | • Inlet pipe blocked | • Inspect the source and unblock the pipe. |
| Overflow from intake chamber | • Gate valve blocked • Blockage in pipeline (e.g., airlock) • Damaged strainer • Clogged strainer | • Remove and clear the valve (replace if necessary). • Check/open the nearest air valve. • Replace the strainer. • Clean the strainer. |
| Dirty water | • Silt in chamber | • Clean out the chamber. |

For river intakes with a weir wall or sump

| Problem | Probable cause | Possible solution |
| --- | --- | --- |
| Little or no water flowing into intake chamber or sump | • Screens on inlet chamber clogged | • Clean the screens. |
| Erosion around side of weir wall | • Insufficient height of wing and cut off walls to prevent flow around the weir | • Construct or raise the wing and cut-off walls to prevent flow around the weir. |
| Undercutting of weir wall on downstream toe or undercutting of sump | • Excessively turbulent flow over weir wall and insufficient width of downstream apron | • Provide a protected apron (constructed of concrete, grouted riprap, etc.) at toe of the weir wall or around the base of the sump. |
| Dirty water | • Excessive sediments upstream of weir wall • Silt in intake chamber or sump | • Clean out any sediment from the area immediately upstream of weir. • Clean out the chamber. • Protect catchment from severe erosion. |

For infiltration galleries

| Problem | Probable cause | Possible solution |
| --- | --- | --- |
| Little or no water flowing into intake chamber or sump | • No water within sandy material in riverbed • Perforated pipe is blocked or damaged | • Excavate the shallow well to determine whether there is water in the sand in the riverbed. • Remove the filter drain and draw-off pipe and reconstruct the infiltration gallery. Consider additional protection for the draw-off pipe. |
| Dirty water | • Filter material (gravel or sand) washed away and replaced with silt or silt-laden sand • Silt in intake chamber or sump | • Check the condition of the filter drain. Replace the filter material if required. Consider additional protection of the filter material. • Clean out the sump. |